## Index Weighting
Hospital Safety Index: Item Weighting Information
Item No. | Items for proposed revised HSI checklist | Hazard(s) | Weighted contribution to each module (%)
| MODULE 2. Elements related to the structural safety of the hospital |  | 100
| 2.1 Prior events and hazards affecting building safety |  | 25
1 | Prior major structural damage or failure of the hospital building(s) | A | 6.25
Safety ratings: Low = Major damage and no repairs; Average = Moderate damage and building only partially repaired; High = Minor or no damage, or building fully repaired.
IF SUCH AN EVENT HAS NOT OCCURRED IN THE VICINITY OF THE HOSPITAL, LEAVE BOXES BLANK.
2 | Hospital built and/or repaired using current safety standards | A | 12.5
Safety ratings: Low = Current safety standards not applied; Average = Current safety standards partially applied; High = Current safety standards fully applied.
3 | Effect of remodeling or modification on the structural behavior of the hospital | A | 6.25
Safety ratings: Low = Major remodelling or modifications have been carried out with major compromising effect on the performance of the structure; Average = Moderate remodelling and/or modifications with minor effect on the performance of the structure; High = Minor remodelling and/or modifications; no modifications were carried out; or major remodelling and/or modification enhancing the structural behaviour or having no negative effect.
| 2.2 Building integrity |  | 75
4 | Structural system design | A | 7.5
Safety ratings: Low = Poor structural system design; Average = Moderate structural system design; High = Good structural system design.
5 | Condition of the building | A | 7.5
Safety ratings: Low = Cracks on the ground and first floors; Major deterioration caused by weathering or normal ageing; Average = Some deterioration caused only by weathering or normal ageing; High = No deterioration or cracks observed.
6 | Condition of the construction materials | A | 6
Safety ratings: Low = Rust with flaking; cracks larger than 3 mm (concrete), excessive deformations (steel and wood); Average = Cracks between 1 and 3 mm present (concrete), moderate and visible deformations (steel and wood) or rust with no flaking; High = Cracks less than 1 mm (concrete), no visible deformations; no rust.
7 | Interaction of nonstructural elements with the structure | A | 4.5
Safety ratings: Low = Partition walls rigidly attached to the structure, suspended ceilings or facades interacting with the structures, damage would have significant effect on the structure; Average = Some of the preceding nonstructural elements interacting with the structures, damage would not affect the structure; High = There are no nonstructural elements affecting the structure.
8 | Proximity of buildings (for earthquake-induced pounding) | E | 2.25
Safety ratings: Low = Separation is less than 0.5% of the height of the shorter of two adjacent buildings; Average = Separation is between 0.5% and 1.5% of the height of the shorter of two adjacent buildings; High = Separation is more than 1.5% of the height of the shorter of two adjacent buildings.
IF THE HOSPITAL IS NOT IN A HIGH/MODERATESEISMIC ZONE, THEN LEAVE BOXES BLANK.
9 | Proximity of buildings (wind tunnel effect and fire) | A | 2.25
Safety ratings: Low = Separation less than 5 m; Average = Separation between 5 m and 15 m; High = Separation more than 15 m.
10 | Structural redundancy | A | 4.5
Safety ratings: Low = Fewer than three lines of resistance in each direction; Average = Three lines of resistance in each direction or lines without orthogonal orientation; High = More than three lines of resistance in each orthogonal direction of the building.
11 | Structural detailing, including connections | A | 3
Safety ratings: Low = No evidence of engineered building records, or built according to an old design standard; Average = Built according to previous design standards and no retrofitting work to a current standard; High = Built according to a current standard.
12 | Ratio of column strength to beam strength | A | 4.5
Safety ratings: Low = Strength of beams is obviously greater than strength of columns; Average = Strength of beams is similar to strength of columns; High = Strength of columns is greater than strength of beams.
13 | Safety of foundations | A | 6
Safety ratings: Low = No evidence that foundations were designed according to standards (foundation size, soil survey) and/or there is evidence of damage; no plans are available; Average = Little evidence (drawings, soil survey) that foundations were designed according to standards; and/or there is evidence for moderate damage; High = Strong evidence that foundations were designed according to standards with strong evidence of no damage.
14 | Irregularities in building structure plan (rigidity, mass, resistance) | A | 3
Safety ratings: Low = Shapes are irregular and structure is not uniform; Average = Shapes on plan are irregular but structure is uniform; High = Shapes on plan are regular and structure has uniform plan, and there are no elements that would cause significant torsion.
15 | Irregularities in elevation of buildings | A | 3
Safety ratings: Low = Significant discontinuous or irregular elements, significant variation in elevation of buildings; Average = Several discontinuous or irregular elements, some variation in the elevation of buildings; High = No significant discontinuous or irregular elements, little or no variation in elevation of buildings.
16 | Irregularities in height of storeys | A | 3
Safety ratings: Low = Height of storeys differs by more than 20% and there are significant discontinuous or irregular elements; Average = Storeys have similar heights (they differ by less than 20% but more than 5%); High = Storeys are of similar height (they differ by less than 5%).
17 | Structural integrity of roofs | A | 4.5
Safety ratings: Low = Monopitch or flat light roofs, and/or large roof overhangs; Average = Pre-stressed concrete roof, gable roof with gentle slope, satisfactorily connected, no large roof overhangs; High = Reinforced cast in place on concrete roof deck or hipped light roof, satisfactory connections, no large roof overhangs.
18 | Structural resilience to hazards other than earthquakes and strong winds | A (except EW) | 13.5
Safety ratings: Low = Low structural resilience to natural hazards present at the site of the hospital; Average = Satisfactory structural resilience (taking account of structural risk reduction measures in place); High = Good structural resilience (taking account of risk reduction measures in place).
Item No. | Items for proposed revised HSI checklist | Hazard(s) | Weighted contribution of to each module (%)
| MODULE 3: Elements related to the non-structural safety of the hospital |  | 100
| 3.1 Architectural safety |  | 23 | Need to insert new 3.1 and adjust numbering of the headings
19 | Major damage and repair of the nonstructural elements | A | 3
Safety ratings: Low = Major damage and no repairs completed; Average = Moderate damage, building only partially repaired; High = Minor or no damage, or building fully repaired.
IF SUCH AN EVENT HAS NOT OCCURRED IN THE VICINITY OF THE HOSPITAL, LEAVE BOXES BLANK.
20 | Condition and safety of doors, exits and entrances | A | 2
Safety ratings: Low = Doors, exits and entrances in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; entrance width is less than 115 cm; Average = In fair condition, subject to damage but damage would not impede the function of this and other elements, systems or operations; or entrance width is less than 115 cm; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations; and entrance width is equal to or larger than 115 cm.
21 | Condition and safety of windows and shutters | A | 1
Safety ratings: Low = Windows and shutters in poor condition, subject to damage which would impede the function of this and other elements, systems or operations (e.g. weak protective glazing); Average = In fair condition, subject to damage but damage would not impede the function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations; protective glass (e.g. polycarbonate glazing, blast film) has been added in critical wards.
22 | Condition and safety of other elements of the building envelope (e.g. outside walls, facings) | A | 1
Safety ratings: Low = Building envelope in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, subject to damage but damage would not impede the function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
23 | Condition and safety of roofing | A | 2
Safety ratings: Low = Roofing in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, subject to damage but damage to element(s) would not impede function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
24 | Condition and safety of railings and parapets | A | 1
Safety ratings: Low = Railings and parapets in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = Subject to damage but damage to element(s) would not impede the function of this and other elements, systems or operations; High = No or minor potential for damage that would impede the function of this and other elements, systems or operations.
25 | Condition and safety of perimeter walls and fencing | A | 1
Safety ratings: Low = Perimeter walls and fencing in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, subject to damage but damage to element(s) would not impede the function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
26 | Condition and safety of other architectural elements (e.g. cornices, ornaments, chimneys, signs) | A | 1
Safety ratings: Low = Other architectural element(s) in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, element(s) are subject to damage but damage would not impede the function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
27 | Safe conditions for movement outside the hospital buildings | A | 1
Safety ratings: Low = Obstacles or damage to structure or road and walkways will impede vehicle and pedestrian access to buildings or endanger pedestrians; Average = Obstacles or damage to structure or road and walkways will not impede pedestrian access, but will impede vehicle access; High = No obstacles, or potential for only minor or no damage that will not impede pedestrian or vehicle access.
28 | Safe conditions for movement inside the building (e.g. corridors, stairs) | A | 2
Safety ratings: Low = Obstacles and damage to element(s) will impede movement inside the building and endanger occupants; Average = Obstacles or damage to elements will not impede movement of people but will impede movement of stretchers, wheeled equipment; High = No obstacles, potential for no or minor damage which will not impede movement of people or wheeled equipment.
29 | Condition and safety of internal walls and partitions | A | 2
Safety ratings: Low = Internal walls and partitions in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, element(s) are subject to damage but damage would not impede the function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
30 | Condition and safety of false or suspended ceilings | A | 2
Safety ratings: Low = False or suspended ceilings in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, element(s) subject to damage but damage would not impede the function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
IF THE HOSPITAL DOES NOT HAVE FALSE OR SUSPENDED CEILINGS, LEAVE BOXES BLANK.
31 | Condition and safety of the elevator system | A | 1.2
Safety ratings: Low = Elevator system in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, element(s) subject to damage but damage would not impede the function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
IF THERE ARE NO ELEVATORS, LEAVE BOXES BLANK.
32 | Condition and safety of stairways and ramps | A | 2
Safety ratings: Low = In poor condition, subject to damage or there are obstacles, which would impede the function of this and other elements, systems or operations; Average = In fair condition, subject to damage but damage and obstacles would not impede the function of this and other elements, systems or operations; High = In good condition, no obstacles, potential for no or minor damage that would impede the function of this and other elements, systems or operations.
IF THERE ARE NO STAIRS AND RAMPS, LEAVE BOXES BLANK.
33 | Condition and safety of floor coverings | A | 0.8
Safety ratings: Low = Floor coverings in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, subject to damage but damage would not impede function; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
| 3.2 Infrastructure protection, access and physical security |  | 10
34 | Location of hospital’s critical services and equipment in relation to local hazards | A | 2.5
Safety ratings: Low = No protection measures taken; subject to damage, failure and disruption of critical services and hospital operations in emergencies and disasters; Average = Partial measures to protect critical services from local hazards are taken; subject to damage with some disruption of critical services and hospital operations in emergencies or disasters; High = Many measures are taken to protect critical services; high probability that critical services and hospital will operate with no or limited disruption in emergencies and disasters.
35 | Hospital access routes | A | 2.5
Safety ratings: Low = Access routes subject to obstacles and damage that would impede access and the function of other elements, systems or operations; Average = Access routes subject to some obstacles and damage that would not impede access and function; High = No or minor potential for obstacles or damage that would impede access and the function of other elements, systems or operations.
36 | Emergency exits and evacuation routes | A | 2.5
Safety ratings: Low = Exit and evacuation routes are not clearly marked and many are blocked; Average = Some exit and evacuation routes are marked and most are clear of obstacles; High = All exit and evacuation routes are clearly marked and free of obstacles.
37 | Physical security of building, equipment, staff and patients | A | 2.5
Safety ratings: Low = No measures are in place; Average = Some physical security protection is in place (e.g. locked storage for supplies and equipment, asset tracking and inventory control); High = Wide range of security measures in place (e.g. design and layout, physical barriers, access control and door security systems, locked storage for supplies and equipment).
| 3.3 Critical systems |  | 50
| 3.3.1 Electrical systems |  | 10
38 | Capacity of alternative sources of electricity (e.g. generators) | A | 2
Safety ratings: Low = Alternate source(s) is (are) missing, or covers less than 30% of demand in critical areas, or can only be started manually; Average = Alternate source(s) covers 31–70% of demand in critical areas and starts automatically in less than 10 seconds in critical areas; High = Alternate source(s) start(s) automatically in less than 10 seconds and cover(s) more than 70% of demand in critical areas.
39 | Regular tests of alternative sources of electricity in critical areas | A | 1
Safety ratings: Low = Tested at full load every 3 months or more; Average = Tested at full load every 1 to 3 months; High = Tested at full load at least monthly.
40 | Condition and safety of alternative source(s) of electricity | A | 1.5
Safety ratings: Low = No alternate sources; generators are in poor condition;, there are no protective measures; Average = Generators are in fair condition; some measures provide partial protection and security; High = Generators are in good condition, well-secured and in good working order for emergencies.
41 | Condition and safety of electrical equipment, cables and cable ducts | A | 0.8
Safety ratings: Low = Electrical equipment, power lines, cables and ducts are in poor condition, there are no protective measures; Average = Electrical equipment, power lines, cables and ducts are in fair condition; some measures provide partial protection and security; High = Electrical equipment, power lines, cables and ducts are in good condition, well-secured and in good working order.
42 | Redundant system for the local electric power supply | A | 0.8
Safety ratings: Low = There is only one entrance for the local power supply; Average = There are two entrances for the local power supply; High = There are more than two entrances for the local power supply.
43 | Condition and safety of control panels, overload breaker switches and cables | A | 0.5
Safety ratings: Low = Control panels or other elements are in poor condition, there are no protective measures; Average = Control panels or other elements are in fair condition; some measures provide partial protection; High = Control panels or other elements are in good condition, well-protected and in good working order.
44 | Lighting system for critical areas of the hospital | A | 1
Safety ratings: Low = Poor level of lighting; there are no protective measures; Average = Lighting is satisfactory in the critical areas; some measures provide partial protection; High = Good levels of lighting and protection measures in place.
45 | Condition and safety of internal and external lighting systems | A | 0.8
Safety ratings: Low = Internal and external lighting systems are in poor condition, there are no protective measures; Average = In fair condition; some measures provide partial protection; High = In good condition, well-protected and in good working order.
46 | External electrical systems installed for hospital usage | A | 0.8
Safety ratings: Low = No electrical substations installed for hospital demands; Average = Substations installed; some measures provide partial protection, but would be vulnerable to damage or disruption, do not provide enough power to the hospital; High = Electrical substations installed, well-protected, and provide enough power to the hospital in an emergency or disaster.
47 | Emergency maintenance and restoration of electric power supply and alternative sources | A | 0.8
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, but resources are not available; High = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
| 3.3.2 Telecommunication systems |  | 5
48 | Condition and safety of antennas | A | 0.4
Safety ratings: Low = Antennas and bracing in poor condition, there are no protective measures; Average = Antennas and bracing are in fair condition, some measures provide partial protection; High = Antennas and bracing are in good condition, well-secured and protection measures are in place.
IF THERE ARE NO ANTENNAS, LEAVE BOXES BLANK.
49 | Condition and safety of low- and extra-low-voltage systems (Internet and telephone) | A | 0.6
Safety ratings: Low = Low voltage systems in poor condition, there are no protective measures; Average = Low voltage systems in fair condition, some measures provide partial protection; High = Good condition, well-secured and other protection measures in place.
50 | Alternative communication systems | A | 1.25
Safety ratings: Low = Alternate communications systems do not exist, are in poor condition, or do not function; Average = Hospital-wide alternate communications system in fair condition, but is not tested on an annual basis; High = Alternate communication system in good condition and tested at least annually.
51 | Condition and safety of telecommunications equipment and cables | A | 0.25
Safety ratings: Low = Telecommunications equipment and cables are in poor condition; there are no protective measures; Average = Equipment and cables are in fair condition; some measures provide partial protection; High = In good condition, well-secured and protected from hazards.
52 | Effect of external telecommunications systems on hospital communications | A | 0.25
Safety ratings: Low = External telecommunications systems cause major interference with hospital communications; Average = External telecommunications system cause moderate interference with hospital communications; High = External communications cause no interference with hospital communications.
53 | Safety of sites for telecommunication systems | A | 0.5
Safety ratings: Low = Sites for telecommunications systems are in poor condition, at high risk of failure due to hazards; there are no protective measures; Average = Sites in fair condition; some measures provide partial protection; High = Good condition, well-secured and other protective measures in place.
54 | Condition and safety of internal communications systems | A | 1.5
Safety ratings: Low = Internal communications systems do not exist or are in poor condition; Average = Internal communications systems are in fair condition, but there are no alternate systems; High = Internal communications and back-up systems are in good working order.
55 | Emergency maintenance and restoration of standard and alternate communications systems | A | 0.25
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, but resources are not available; High = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
| 3.3.3 Water supply system |  | 10
56 | Water reserves for hospital services and functions | A | 3.5
Safety ratings: Low = Sufficient for 24 hours or less, or water tank does not exist; Average = Sufficient for more than 24 hours but less than 72 hours; High = Guaranteed to cover at least 72 hours.
57 | Location of water storage tanks | A | 1
Safety ratings: Low = The site is vulnerable with high risk of failure (e.g. structural, architectural and/or system vulnerabilities); Average = The site is exposed to moderate risk of failure (e.g. structural, architectural and/or system vulnerabilities); High = The site is not exposed to visually identifiable risks (e.g. structural, architectural and/or system vulnerabilities).
IF THE HOSPITAL DOES NOT HAVE A WATER STORAGE TANK, LEAVE BOXES BLANK.
58 | Safety of the water distribution system | A | 1.2
Safety ratings: Low = Less than 60% are in good operational condition; Average = Between 60% and 80% are in good condition; High = Above 80% are in good condition.
59 | Alternative water supply to the regular water supply | A | 3
Safety ratings: Low = Provides less than 30% of daily demand in an emergency or disaster scenario; Average = Provides 30−80% of daily demand in an emergency or disaster scenario; High = Provides more than 80% of daily demand in an emergency or disaster scenario.
60 | Supplementary pumping system | A | 0.8
Safety ratings: Low = There is no back-up pump and operational capacity does not meet minimum daily demand; Average = Supplementary pumps are in fair condition but would not meet the minimum daily demand for water; High = All supplementary pumps and back-up systems are operational and would meet the minimum demand for water.
61 | Emergency maintenance and restoration of water supply | A | 0.5
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, but resources are not available; High = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
| 3.3.4 Fire protection system |  | 7.5
62 | Condition and safety of the fire protection (passive) system | A | 2.25
Safety ratings: Low = Element(s) are subject to damage, and damage would impede the function of this and other elements, systems or operations; Average = Element(s) are subject to damage but damage would not impede function; High = No or minor potential for damage that would impede the function of this and other elements, systems or operations.
63 | Fire/smoke detection systems | A | 1.875
Safety ratings: Low = No system has been installed; Average = System is partially installed, or infrequently maintained and tested; High = System is installed and well-maintained and tested frequently.
64 | Fire suppression systems (automatic and manual) | A | 1.875
Safety ratings: Low = No system has been installed; inspections do not occur; Average = System is partially installed, or system is installed, but no maintenance or testing; inspections are incomplete or outdated; High = System is fully installed and regularly maintained and tested frequently; inspections are complete and up to date.
65 | Water supply for fire suppression | A | 1.125
Safety ratings: Low = A source of permanent supply which could be used for fire suppression does not exist; Average = A source of permanent supply of water is available for fire suppression; there is limited capacity available, and no maintenance and testing has been conducted; High = A source of permanent water supply with significant capacity for fire suppression is available, regularly maintained and frequently tested.
66 | Emergency maintenance and restoration of the fire protection system | A | 0.375
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, but resources are not available; High = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
| 3.3.5 Waste management systems |  | 2.5
67 | Safety of nonhazardous wastewater systems | A | 0.375
Safety ratings: Low = System for nonhazardous wastewater disposal does not exist or is in poor condition; Average = System is in fair condition, but little or no evidence of compliance and maintenance; High = Wastewater disposal system is in good condition with good capacity and evidence of compliance and maintenance.
68 | Safety of hazardous wastewater and liquid waste | A | 1
Safety ratings: Low = System for hazardous wastewater disposal does not exist or is in poor condition; Average = System in fair condition but little or no evidence of compliance and maintenance; High = Disposal system has good capacity and evidence of compliance and maintenance.
69 | Safety of nonhazardous solid waste system | A | 0.375
Safety ratings: Low = System for solid waste disposal does not exist or is in poor condition; Average = System is in fair condition, but little or no evidence of compliance and maintenance; High = Disposal system is in good condition with good capacity and evidence of compliance and maintenance.
70 | Safety of hazardous solid waste system | A | 0.5
Safety ratings: Low = System for hazardous waste disposal does not exist or is in poor condition; Average = System is in fair condition but little or no evidence of compliance and maintenance; High = Disposal system is in good condition with good capacity and evidence of compliance and maintenance.
71 | Emergency maintenance and restoration of all types of hospital waste management systems | A | 0.25
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, but resources are not available; High = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
| 3.3.6 Fuel storage systems (e.g. gas, gasoline and diesel) |  | 5
72 | Fuel reserves | A | 1.5
Safety ratings: Low = Sufficient for 24 hours or less, or fuel tank does not exist; Average = Sufficient for more than 24 hours but less than 72 hours; High = Guaranteed to cover at least 72 hours.
73 | Condition and safety of above-ground fuel tanks and/or cylinders | A | 1.5
Safety ratings: Low = Tanks are in poor condition; there are no anchors or tank enclosure; tanks are not safely located with respect to hazards; Average = Tanks are in fair condition, anchors and bracing are inadequate for major hazards; tank enclosure has some safety and security measures; High = Tanks are in good condition; anchors and bracing are in good condition for major hazards; the tank enclosure has adequate safety and security.
IF THE HOSPITAL DOES NOT HAVE THESE SERVICES, LEAVE BLANK.
74 | Safe location of fuel storage away from hospital buildings | A | 1
Safety ratings: Low = Fuel storage is not accessible and is not located in a secure site; Average = Site in fair condition and in fair location in relation to hazards; some measures provide partial protection; High = In good condition and good location, well-secured and other protection measures in place; fuel tanks are accessible.
IF THERE IS NO FUEL TANK, LEAVE BOXES BLANK.
75 | Condition and safety of the fuel distribution system (valves, hoses, and connections) | A | 0.75
Safety ratings: Low = Less than 60% of the system is in safe operational condition; Average = between 60% and 90% of the system is in good operational condition and has automatic shut-off valves; High = More than 90% of the system is in good operational condition and has automatic shut-off valves.
IF THERE IS NO FUEL DISTRIBUTION TANK, LEAVE BOXES BLANK.
76 | Emergency maintenance and restoration of fuel reserves | A | 0.25
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, but resources are not available; High = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
| 3.3.7 Medical gases systems |  | 5
77 | Location of storage areas for medical gases | A | 1
Safety ratings: Low = No sites reserved for medical gases, or sites for medical gases are at high risk of failure due to hazards; there are no protective measures, and storage is not accessible; Average = Reserved areas in fair condition and fair location; some measures provide partial protection; High = In good condition, well-secured and other protective measures are in place; storage is accessible.
78 | Safety of storage areas for the medical gas tanks and/or cylinders | A | 1
Safety ratings: Low = Medical gas tanks and cylinders in storage areas are poor condition; no protection measures, not secured; personnel are not trained to operate medical gas and fire extinguishing equipment; Average = Medical gas tanks and cylinders in storage areas are in fair condition, some measures provide partial protection; the quality of anchors and braces is inadequate; personnel are trained to operate equipment; High = Good condition, well-secured and protected, anchors are of good quality for major hazards; medical gas and fire extinguishing equipment operated by qualified personnel.
79 | Condition and safety of medical gas distribution system (e.g. valves, pipes, connections) | A | 1
Safety ratings: Low = Less than 60% of the system is in good working condition; Average = Between 60% and 80% of the system is in good working condition; High = More than 80% of the system is in good working condition.
80 | Condition and safety of medical gas cylinders and related equipment in the hospital | A | 1
Safety ratings: Low = Medical gas tanks and cylinders in hospital areas are in poor condition, no protective measures; not secured; Average = Medical gas tanks and cylinders are in fair condition; the quality of anchors and braces is inadequate; some measures provide partial protection; High = Good condition, well-secured and protected; anchors are of good quality for major hazards.
81 | Availability of alternative sources of medical gases | A | 0.75
Safety Ratings: Low = Alternative sources are not available; Average = Alternative sources in place but delivery of supplies takes longer than 15 days; High = Sufficient alternative sources are available at short notice (less than 15 days).
82 | Emergency maintenance and restoration of medical gas systems. | A | 0.25
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, and personnel have been trained, but resources are not available; High = Procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
| 3.3.8 Heating, ventilation, and air-conditioning (HVAC) systems |  | 5
83 | Adequate location of enclosures for HVAC equipment | A | 0.75
Safety ratings: Low = HVAC enclosures are not accessible and they are not located in a safe site; there are no protective measures; Average = HVAC enclosures are accessible, located at a safe site; some measures provide partial protection from hazards; High = HVAC enclosures are accessible, in a safe location and protected from hazards.
84 | Safety of enclosures for HVAC equipment | A | 1
Safety ratings: Low = HVAC equipment is not accessible; no protective measures for safe operation and maintenance; Average = HVAC is accessible; some measures provide partial protection; High = HVAC equipment is accessible, wide range of protection measures in place.
85 | Safety and operating condition of HVAC equipment (e.g. boiler, exhaust) | A | 1
Safety ratings: Low = HVAC equipment in poor condition, not maintained; Average = HVAC equipment in fair condition; some measures provide partial protection, but no regular maintenance; High = Good condition, well-secured and protected from hazards (e.g. anchors are of good quality); regular maintenance and testing of controls and alarms conducted.
86 | Adequate supports for ducts and review of flexibility of ducts and piping that cross expansion joints | A | 0.5
Safety ratings: Low = Supports are lacking and connections are rigid; Average = Supports are in fair condition or connections are flexible; High = Supports are in good condition and connections are flexible.
87 | Condition and safety of pipes, connections and valves | A | 0.5
Safety ratings: Low = Less than 60% of pipes are in good condition; limited protective measures against hazards; Average = Between 60% and 80% are in good condition; some measures provide partial protection against hazards; High = Above 80% are in good condition and are well-secured and protected against hazards.
88 | Condition and safety of air-conditioning equipment | A | 0.5
Safety ratings: Low = Air-conditioning units in poor condition, not secured; Average = Air-conditioning units are in fair condition; some measures provide partial protection (e.g. quality of anchors and braces is inadequate); High = Good condition, well-secured and protected from hazards (e.g. anchors are of good quality).
89 | Operation of air-conditioning system (including negative pressure areas) | A | 0.5
Safety ratings: Low = Air-conditioning system has no capability for establishing zones of the hospital; Average = Air-conditioning system can establish zones, but has no capacity to separate air circulating between high-risk areas and other areas of the hospital; High = Air-conditioning system can isolate air from high-risk areas; negative pressure rooms are available.
90 | Emergency maintenance and restoration of the HVAC systems | A | 0.25
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, but resources are not available; High = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
| 3.4 Equipment and supplies |  | 17
| 3.4.1 Office and storeroom furnishings and equipment (fixed and movable) |  | 1.7
91 | Safety of shelving and shelf contents | A | 0.85
Safety ratings: Low = Shelving is not safely located (or in seismic and wind-prone areas not attached to walls in in more than 20% of cases); Average = Shelving is safely located (and attached to walls in seismic and wind-prone areas) and contents are secured in 20−80% of cases; High = More than 80% of shelving and the contents of shelves are safely located, attached to walls, and contents are secured.
92 | Safety of computers and printers | A | 0.85
Safety ratings: Low = No measures to protect computers from hazards are in place; Average = Computers are in safe locations, some measures offer partial protection from hazards; High = Computers are in safe locations, well-secured and good protective measures in place.
| 3.4.2 Medical and laboratory equipment and supplies used for diagnosis and treatment |  | 15.3
93 | Safety of medical equipment in operating theatres and recovery rooms | A | 0.765
Safety ratings: Low = The operating theatres are in an unsafe location, equipment is lacking or in poor condition or there are no protective measures; Average = The operating theatres are in a safe location, equipment is in fair condition, and some measures provide partial protection; High = Operating theatres are in a safe location, equipment is in good condition, is well-secured and measures provide protection.
94 | Condition and safety of radiology and imaging equipment | A | 0.765
Safety ratings: Low = The radiology and imaging equipment is not in a safe location, equipment is lacking or in poor condition, or there are no protective measures; Average = The equipment is in a safe location, is in fair condition, and some measures offer partial protection; High = Equipment is in a safe location, is in good condition, well-secured and measures provide good protection.
95 | Condition and safety of laboratory equipment and supplies | A | 0.765
Safety ratings: Low = Biosafety measures are poor, laboratory equipment is lacking or in poor condition, or there are no protective measures; Average = Biosafety measures are in place, the equipment is in fair condition, and some measures provide partial protection; High = Biosafety measures in place, equipment is in good condition, well-secured and measures provide good protection.
96 | Condition and safety of medical equipment in emergency care services unit | A | 0.765
Safety ratings: Low = The medical equipment is lacking or in poor condition, or there are no protective measures; Average = The equipment is in fair condition and some measures provide partial protection; High = Equipment is in good condition, well-secured and measures provide good protection.
97 | Condition and safety of medical equipment in intensive or intermediate care unit | A | 0.765
Safety ratings: Low = The medical equipment is lacking or in poor condition, or there are no protective measures; Average = The equipment is in fair condition and some measures provide partial protection; High = Equipment is in good condition, is well-secured and measures provide good protection.
98 | Condition and safety of equipment and furnishings in the pharmacy | A | 0.765
Safety ratings: Low = The equipment in the pharmacy is lacking or in poor condition, or there are no protective measures; Average = The equipment is in fair condition and some measures provide partial protection; High = Equipment is in good condition, is well-secured and measures provide good protection.
99 | Condition and safety of equipment and supplies in the sterilization services | A | 0.765
Safety ratings: Equipment is lacking or in poor condition, or there are no protective measures; Average = Equipment is in fair condition and some measures provide partial protection; High = Equipment is in good condition, is well-secured and measures provide good protection.
100 | Condition and safety of medical equipment for obstetric emergencies and neonatal care | A | 0.306
Safety ratings: Low = Equipment is lacking or in poor condition, or there are no protective measures; Average = Equipment is in fair condition and some measures provide partial protection; High = Equipment is in good condition, is well-secured and measures provide good protection.
101 | Condition and safety of medical equipment and supplies emergency care for burns | A | 0.306
Safety ratings: Low = Equipment is lacking, is in poor condition, or there are no protective measures; Average = Equipment is in fair condition and some measures provide partial protection; High = Equipment is in good condition, is well-secured and measures provide good protection.
102 | Condition and safety of medical equipment for nuclear medicine and radiation therapy | A | 0.306
Safety ratings: Low = Equipment is lacking, is in poor condition, or there are no protective measures; Average = Equipment is in fair condition and some measures provide partial protection; High = Equipment is in good condition, is well-secured and measures provide good protection.
IF THE HOSPITAL DOES NOT HAVE THESE SERVICES, LEAVE BLANK.
103 | Condition and safety of medical equipment in other services | A | 0.306
Safety ratings: Low = More than 30% of equipment is at risk of material or functional failure and/or equipment puts the entire service’s operation at direct or indirect risk; Average = Between 10% and 30% of equipment is at risk of loss; High = Less than 10% of equipment is at risk of loss.
104 | Medicines and supplies | A | 1.836
Safety ratings: Low = Nonexistent; Average = Supply covers less than 72 hours at maximum capacity; High = Supply guaranteed for at least 72 hours at maximum hospital capacity.
105 | Sterilized instruments and other materials | A | 1.836
Safety ratings: Low = Nonexistent; Average = Supply cover less than 72 hours at maximum capacity; High = Supply is guaranteed for at least 72 hours at maximum hospital capacity.
106 | Medical equipment specifically used in emergencies and disasters | A | 1.53
Safety ratings: Low = Nonexistent; Average = Supply covers less than 72 hours at maximum hospital capacity; High = Supply guaranteed for at least 72 hours at maximum hospital capacity.
107 | Supply of medical gases | A | 1.836
Safety ratings: Low = Less than 10 days’ supply; Average = Supply for between 10 and 15 days; High = Supply for at least 15 days.
108 | Mechanical volume ventilators | A | 0.306
Safety ratings: Low = Nonexistent; Average = Supply covers less than 72 hours at maximum hospital capacity; High = Supply guaranteed for at least 72 hours at maximum hospital capacity.
109 | Electromedical equipment | A | 0.306
Safety ratings: Low = Nonexistent; Average = Supply covers less than 72 hours at maximum hospital capacity; High = Supply guaranteed for at least 72 hours at maximum hospital capacity.
110 | Life-support equipment | A | 0.765
Safety ratings: Low = Nonexistent; Average = Supply covers less than 72 hours at maximum hospital capacity; High = Supply guaranteed for at least 72 hours at maximum hospital capacity.
111 | Supplies, equipment or crash carts for cardiopulmonary arrest | A | 0.306
Safety ratings: Low = Nonexistent; Average = Supplies and equipment for cardiopulmonary emergencies (or crash carts) in good condition but cover less than 72 hours at maximum hospital capacity; High = Supplies and equipment for cardiopulmonary emergencies (or crash carts) guaranteed in good condition and adequate supplies for at least 72 hours at maximum hospital capacity.
Item No. | Items for proposed revised HSI checklist | Hazard(s) | Weighted contribution of each item to each module
| MODULE 4. Emergency and disaster management |  | 100
| 4.1 Coordination of emergency and disaster management activities |  | 15
112 | Hospital Emergency/Disaster Committee | A | 3
Safety ratings: Low = Committee does not exist, or 1–3 departments or disciplines represented; Average = Committee exists with 4–5 departments or disciplines represented, but is not fulfilling functions effectively; High = Committee exists with 6 or more departments or disciplines represented and is fulfilling functions effectively.
113 | Committee member responsibilities and training | A | 1.05
Safety ratings: Low = Committee does not exist or members are untrained and responsibilities not assigned; Average = Members have received training and have been officially assigned; High = All members are trained and are actively fulfilling their roles and responsibilities.
114 | Designated emergency and disaster management coordinator | A | 1.2
Safety ratings: Low = There is no staff member who has been assigned responsibilities as the emergency/disaster management coordinator; Average = Emergency/disaster management coordination tasks have been assigned to a staff member, but it is not his/her main task; High = A staff member is assigned the emergency and disaster management coordination responsibilities as his/her main task, and is fulfilling the role of implementing the hospital’s preparedness programme.
115 | Preparedness programme for strengthening emergency and disaster response and recovery | A | 3.75
Safety ratings: Low = A programme for strengthening preparedness, response and recovery does not exist or, if it exists, no preparedness activities are being implemented; Average = A programme for strengthening preparedness, response and recovery exists and some activities are being implemented; High = A programme for strengthening preparedness, response and recovery is being fully implemented under the leadership of the Hospital Emergency/Disaster Committee.
116 | Hospital incident management system | A | 1.2
Safety ratings: Low = No arrangements for hospital incident management exist; Average = Staff assigned to key hospital incident management positions but with no written procedures to operationalize its functions; High = Hospital incident management procedures exist and are fully operational with properly trained personnel to assume different coordination roles and responsibilities.
117 | Emergency Operations Centre (EOC) | A | 1.8
Safety ratings: Low = The EOC is not designated or is in an unsafe or insecure location; Average = The designated EOC is in a safe, secure and accessible location, but would have limited operational capacity immediately in an emergency; High = The EOC is in a safe, secure and accessible location with immediate operational capacity.
118 | Coordination mechanisms and cooperative arrangements with local emergency/disaster management agencies | A | 1.5
Safety ratings: Low = No arrangements exist; Average = Arrangements exist but are not fully operational; High = Arrangements exist and are fully operational.
119 | Coordination mechanisms and cooperative arrangements with the health-care network | A | 1.5
Safety ratings: Low = No arrangements exist; Average = Arrangements exist but are not fully operational; High = Arrangements exist and are fully operational.
| 4.2 Hospital emergency and disaster management response and recovery planning |  | 18
120 | Hospital emergency or disaster response plan | A | 6.3
Safety ratings: Low = Plan is not documented; Average = Documented plan is complete, but is not easily accessible, not up to date (more than 12 months since the last update); High = Plan is complete, easily accessible, reviewed/updated at least annually, and resources are available to implement the plan.
121 | Hazard-specific subplans | A | 5.4
Safety ratings: Low = Hazard-specific response subplans are not documented; Average = Documented plans are complete but not easily accessible, not up to date (more than 12 months since last review/update); High = Documented plans are complete, reviewed/updated at least annually, and resources are available to implement the plans.
122 | Procedures to activate and deactivate plans | A | 1.26
Safety ratings: Low = Procedures do not exist or exist only as a document; Average = Procedures exist, personnel have been trained, but procedures are not updated or tested annually; High = Up-to-date procedures exist, personnel have been trained, and procedures have been tested at least annually.
123 | Hospital emergency and disaster response plan exercises, evaluation and corrective actions | A | 3.6
Safety ratings: Low = Response plan and subplans have not been tested; Average = Response plan or subplans are tested, but are not tested at least annually; High = Response plan or subplans are tested at least annually and updated according to the exercise results.
124 | Hospital recovery plan | A | 1.44
Safety ratings: Low = Recovery plan is not documented; Average = Documented plan is complete but not easily accessible, not up to date (more than 12 months since last review/update); High = Documented plan is complete, easily accessible, and reviewed/updated at least annually.
| 4.3 Communication and information management |  | 7
125 | Emergency internal and external communication | A | 2.8
Safety ratings: Low = Central internal and external communication system functions inconsistently or incompletely; operators are not trained in emergency communication; Average = System functions appropriately, operators have received some training in emergency communication, tests are not conducted at least annually; High = System functions completely and operators are fully trained in emergency use, and tests of the system are conducted at least annually.
126 | External stakeholder directory | A | 1.75
Safety ratings: Low = Directory of external stakeholders does not exist; Average = Directory exists but is not current (more than 3 months since it was updated); High = Directory is available, is up to date and is held by key emergency response staff.
127 | Procedures for communicating with the public and media | A | 1.4
Safety ratings: Low = Procedures do not exist, no spokesperson nominated; Average = Procedures exist and nominated spokespersons have been trained; High = Procedures exist, nominated spokespersons have been trained, and procedures have been tested at least annually.
128 | Management of patient information | A | 1.05
Safety ratings: Low = Procedures for emergency situations do not exist; Average = Procedures for emergency situations exist and personnel have been trained but no resources are available; High = Procedures for emergency situations exist, personnel have been trained, and resources are in place for implementation.
| 4.4 Human resources |  | 20
129 | Staff contact list | A | 3
Safety ratings: Low = Contact list does not exist; Average = List exists, but is not current (more than 3 months since it was updated); High = List is available and up to date.
130 | Staff availability | A | 8
Safety ratings: Low = Less than 50% of staff are available to run each department adequately; Average = 50−80% of staff are available; High = 80−100% of staff are available.
131 | Mobilization and recruitment of personnel during an emergency or disaster | A | 3
Safety ratings: Low = Procedures do not exist or exist only in a document; Average = Procedures exist and personnel have been trained, but the human resources for an emergency situation are not available; High = Procedures exist, personnel have been trained, and the human resources are available to meet anticipated needs in an emergency.
132 | Duties assigned to personnel for emergency or disaster response and recovery | A | 5
Safety ratings: Low = Emergency assignments do not exist or are not documented; Average = Duties are identified, some (but not all) personnel receive written assignments or training; High = Written duties are assigned, and training or an exercise is conducted for all personnel at least annually.
133 | Well-being of hospital personnel during an emergency or disaster | A | 1
Safety ratings: Low = A designated space and measures do not exist; Average = Space has been designated, but measures cover less than 72 hours; High = Measures are ensured for at least 72 hours.
| 4.5 Logistics and finance |  | 8
134 | Agreements with local suppliers and vendors for emergencies and disasters | A | 2
Safety ratings: Low = No arrangements exist; Average = Arrangements exist, but are not fully operational; High = Arrangements exist and are fully operational.
135 | Transportation during an emergency | A | 2
Safety ratings: Low = Ambulances and other vehicles and modes of transportation are not available; Average = Some vehicles are available, but not in sufficient numbers for a major emergency or disaster; High = Appropriate vehicles in sufficient numbers are available during emergencies/disasters.
136 | Food and drinking-water during an emergency | A | 1.6
Safety ratings: Low = Procedures for food and drinking-water for emergencies are non-existent; Average = Procedures exist, food and drinking-water is guaranteed for less than 72 hours; High = Food and drinking-water for emergencies is guaranteed for at least 72 hours.
137 | Financial resources for emergencies and disasters | A | 2.4
Safety ratings: Low = Emergency budget or mechanism to access emergency funds is not in place; Average = Funds are budgeted and mechanisms are available but cover less than 72 hours; High = Sufficient funds are guaranteed for 72 hours or more.
| 4.6 Patient care and support services |  | 25
138 | Continuity of emergency and critical care services | A | 5
Safety ratings: Low = Procedures do not exist or exist only as a document; Average = Procedures exist, personnel have been trained but would not be available at all times; High = Procedures exist, personnel have been trained, and resources are available to implement procedures at maximum hospital capacity for emergency and disaster situations at all times.
139 | Continuity of essential clinical support services | A | 3.75
Safety ratings: Low = Procedures do not exist or exist only as a document; Average = Procedures exists and personnel have been trained but would not be available at all times; High = Procedures exists, personnel have been trained, and resources are available to implement procedures at maximum hospital capacity for emergency and disaster situations at all times.
140 | Expansion of usable space for mass casualty incidents | A | 2.5
Safety ratings: Low = Space for expansion has not been identified; Average = Space has been identified; equipment, supplies and procedures are available to carry out the expansion and staff have been trained, but testing has not been conducted; High = Procedures exist and have been tested, personnel have been trained, and equipment, supplies and other resources are available to carry out the expansion of space.
141 | Triage for major emergencies and disasters | A | 3
Safety ratings: Low = Designated triage location or procedures do not exist; Average = Triage location and procedures exist and personnel have been trained, but procedures have not been tested for emergency and disaster situations; High = Location and procedures exist and have been tested, personnel have been trained, and resources are in place to implement at maximum hospital capacity in emergency and disaster situations.
142 | Triage tags and other logistical supplies for mass casualty incidents | A | 0.75
Safety ratings: Low = Nonexistent; Average = Supply covers less than 72 hours of maximum hospital capacity; High = Supply guaranteed for at least 72 hours of maximum hospital capacity.
143 | System for referral, transfer and reception of patients | A | 2.5
Safety ratings: Low = Procedures do not exist or exist only as a document; Average = Procedures exist and personnel have been trained, but procedures have not been tested for emergency or disaster situations; High = Procedures exist and have been tested, personnel have been trained, and resources are available to implement measures at maximum hospital capacity in emergency or disaster situations.
144 | Infection surveillance, prevention, and control procedures | A | 3.75
Safety ratings: Low = Policies and procedures do not exist; standard precautions for infection prevention and control are not followed routinely; Average = Policies and procedures exist, standard precautions are routinely followed, personnel have been trained, but the level of resources required for emergency and disaster situations, including epidemics, is not available; High = Policies and procedures exist, infection prevention and control measures are in place, personnel have been trained, and resources are available to implement measures at maximum hospital capacity in emergency and disaster situations.
145 | Psychosocial services | A | 2.5
Safety ratings: Low = Procedures do not exist or exist only as a document; Average = Procedures exist and personnel have been trained, but the level of resources required for emergency and disaster situations is not available; High = Procedures exist, personnel have been trained, and resources are available for implementation of procedures at maximum hospital capacity in emergency and disaster situations.
146 | Post-mortem procedures in a mass fatality incident | A | 1.25
Safety ratings: Low = Procedures for a mass fatality incident do not exist or exist only as a document; Average = Procedures exist and personnel have been trained, but the level of resources required for emergency and disaster situations is not available; High = Procedures exist, personnel have been trained, and resources are available for implementation of procedures at maximum hospital capacity in emergency and disaster situations
| 4.7 Evacuation, decontamination and security |  | 7
147 | Evacuation plan | A | 3.5
Safety ratings: Low = Plan does not exist or exists only as a document; Average = Plan exists and personnel have been trained in procedures, but tests are not conducted regularly; High = Plan exists, personnel have been trained, and evacuation drills are held at least annually.
148 | Decontamination for chemical/biological hazards | BC | 1.05
Safety ratings: Low = No personal protective equipment is available for immediate use by hospital staff, or no decontamination area exists; Average = Personal protective equipment is available for immediate use, decontamination areas are established, staff training and drills are not conducted annually; High = Personal protective equipment is available for immediate use, decontamination areas are established and personnel are trained and tested at least annually.
149 | Personal protection equipment and isolation for infectious diseases and epidemics | B | 0.35
Safety ratings: Low = No personal protective equipment is available for immediate use by hospital staff, or no isolation area exists; Average = Supply is available for immediate use, but is sufficient for less than 72 hours of maximum hospital capacity, isolation areas are established, staff training and testing of procedures are not conducted annually; High = Supply is guaranteed for at least 72 hours of maximum hospital capacity and alternate sources are in place for resupply, isolation areas are established, staff training and testing of procedures are conducted at least annually.
150 | Emergency security procedures | A | 1.75
Safety ratings: Low = Emergency security procedures do not exist or exist only as a document; Average = Documented procedures exist and personnel have been trained in emergency security procedures but testing is not conducted at least annually; High = Personnel are trained and tests of the documented procedures are held at least annually.
151 | Computer system network security | A | 0.35
Safety ratings: Low = The hospital does not have a computer security system plan and procedures in place; Average = The hospital has a basic cyber security plan in place but it is not monitored and updated regularly; High = The hospital has a cyber security plan in place and it is updated regularly.

## Calculator 1
Hospital Safety Index: Page 1_Step 1-2 (Safety Ratings)
Step 1: Enter a number "1" in the corresponding YELLOW cell of each item. Some rows would stay in BLANK only if there is a note in CAPITAL LETTERS.
MODULE 2. Elements related to the structural safety of the hospital
2.1 Prior events and hazards affecting building safety | Control | Safety level
|  | Low | Average | High
1. Prior major structural damage or failure of the hospital building(s) | BLANK
Safety ratings: Low = Major damage and no repairs; Average = Moderate damage and building only partially repaired; High = Minor or no damage, or building fully repaired.
IF SUCH AN EVENT HAS NOT OCCURRED IN THE VICINITY OF THE HOSPITAL, LEAVE BOXES BLANK.
2. Hospital built and/or repaired using current safety standards | ERROR
Safety ratings: Low = Current safety standards not applied; Average = Current safety standards partially applied; High = Current safety standards fully applied.
3. Effect of remodeling or modification on the structural behavior of the hospital | ERROR
Safety ratings: Low = Major remodelling or modifications have been carried out with major compromising effect on the performance of the structure; Average = Moderate remodelling and/or modifications with minor effect on the performance of the structure; High = Minor remodelling and/or modifications; no modifications were carried out; or major remodelling and/or modification enhancing the structural behaviour or having no negative effect.
2.2 Building integrity | Control | Safety level
|  | Low | Average | High
4. Structural system design | ERROR
Safety ratings: Low = Poor structural system design; Average = Moderate structural system design; High = Good structural system design.
5. Condition of the building | ERROR
Safety ratings: Low = Cracks on the ground and first floors; Major deterioration caused by weathering or normal ageing; Average = Some deterioration caused only by weathering or normal ageing; High = No deterioration or cracks observed.
6. Condition of the construction materials | ERROR
Safety ratings: Low = Rust with flaking; cracks larger than 3 mm (concrete), excessive deformations (steel and wood); Average = Cracks between 1 and 3 mm present (concrete), moderate and visible deformations (steel and wood) or rust with no flaking; High = Cracks less than 1 mm (concrete), no visible deformations; no rust.
7. Interaction of nonstructural elements with the structure | ERROR
Safety ratings: Low = Partition walls rigidly attached to the structure, suspended ceilings or facades interacting with the structures, damage would have significant effect on the structure; Average = Some of the preceding nonstructural elements interacting with the structures, damage would not affect the structure; High = There are no nonstructural elements affecting the structure.
8. Proximity of buildings (for earthquake-induced pounding) | BLANK
Safety ratings: Low = Separation is less than 0.5% of the height of the shorter of two adjacent buildings; Average = Separation is between 0.5% and 1.5% of the height of the shorter of two adjacent buildings; High = Separation is more than 1.5% of the height of the shorter of two adjacent buildings.
IF THE HOSPITAL IS NOT IN A HIGH/MODERATESEISMIC ZONE, THEN LEAVE BOXES BLANK.
9. Proximity of buildings (wind tunnel effect and fire) | ERROR
Safety ratings: Low = Separation less than 5 m; Average = Separation between 5 m and 15 m; High = Separation more than 15 m.
10. Structural redundancy | ERROR
Safety ratings: Low = Fewer than three lines of resistance in each direction; Average = Three lines of resistance in each direction or lines without orthogonal orientation; High = More than three lines of resistance in each orthogonal direction of the building.
11. Structural detailing, including connections | ERROR
Safety ratings: Low = No evidence of engineered building records, or built according to an old design standard; Average = Built according to previous design standards and no retrofitting work to a current standard; High = Built according to a current standard.
12. Ratio of column strength to beam strength | ERROR
Safety ratings: Low = Strength of beams is obviously greater than strength of columns; Average = Strength of beams is similar to strength of columns; High = Strength of columns is greater than strength of beams.
13. Safety of foundations | ERROR
Safety ratings: Low = No evidence that foundations were designed according to standards (foundation size, soil survey) and/or there is evidence of damage; no plans are available; Average = Little evidence (drawings, soil survey) that foundations were designed according to standards; and/or there is evidence for moderate damage; High = Strong evidence that foundations were designed according to standards with strong evidence of no damage.
14. Irregularities in building structure plan (rigidity, mass, resistance) | ERROR
Safety ratings: Low = Shapes are irregular and structure is not uniform; Average = Shapes on plan are irregular but structure is uniform; High = Shapes on plan are regular and structure has uniform plan, and there are no elements that would cause significant torsion.
15. Irregularities in elevation of buildings | ERROR
Safety ratings: Low = Significant discontinuous or irregular elements, significant variation in elevation of buildings; Average = Several discontinuous or irregular elements, some variation in the elevation of buildings; High = No significant discontinuous or irregular elements, little or no variation in elevation of buildings.
16. Irregularities in height of storeys | ERROR
Safety ratings: Low = Height of storeys differs by more than 20%; Average = Storeys have similar heights (they differ by less than 20% but more than 5%); High = Storeys are of similar height (they differ by less than 5%).
17. Structural integrity of roofs | ERROR
Safety ratings: Low = Monopitch or flat light roofs, and/or large roof overhangs; Average = Pre-stressed concrete roof, gable roof with gentle slope, satisfactorily connected, no large roof overhangs; High = Reinforced cast in place on concrete roof deck or hipped light roof, satisfactory connections, no large roof overhangs.
18. Structural resilience to hazards other than earthquakes and strong winds | ERROR
Safety ratings: Low = Low structural resilience to natural hazards present at the site of the hospital; Average = Satisfactory structural resilience (taking account of structural risk reduction measures in place); High = Good structural resilience (taking account of risk reduction measures in place).
MODULE 3: Elements related to the non-structural safety of the hospital
3.1. Architectural safety | Control | Safety level
|  | Low | Average | High
19. Major damage and repair of the nonstructural elements | BLANK
Safety ratings: Low = Major damage and no repairs completed; Average = Moderate damage, building only partially repaired; High = Minor or no damage, or building fully repaired.
IF SUCH AN EVENT HAS NOT OCCURRED IN THE VICINITY OF THE HOSPITAL, LEAVE BOXES BLANK.
20. Condition and safety of doors, exits and entrances | ERROR
Safety ratings: Low = Doors, exits and entrances in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; entrance width is less than 115 cm; Average = In fair condition, subject to damage but damage would not impede the function of this and other elements, systems or operations; or entrance width is less than 115 cm; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations; and entrance width is equal to or larger than 115 cm.
21. Condition and safety of windows and shutters | ERROR
Safety ratings: Low = Windows and shutters in poor condition, subject to damage which would impede the function of this and other elements, systems or operations (e.g. weak protective glazing); Average = In fair condition, subject to damage but damage would not impede the function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations; protective glass (e.g. polycarbonate glazing, blast film) has been added in critical wards.
22. Condition and safety of other elements of the building envelope (e.g. outside walls, facings) | ERROR
Safety ratings: Low = Building envelope in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, subject to damage but damage would not impede the function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
23. Condition and safety of roofing | ERROR
Safety ratings: Low = Roofing in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, subject to damage but damage to element(s) would not impede function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
24. Condition and safety of railings and parapets | ERROR
Safety ratings: Low = Railings and parapets in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = Subject to damage but damage to element(s) would not impede the function of this and other elements, systems or operations; High = No or minor potential for damage that would impede the function of this and other elements, systems or operations.
25. Condition and safety of perimeter walls and fencing | ERROR
Safety ratings: Low = Perimeter walls and fencing in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, subject to damage but damage to element(s) would not impede the function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
26. Condition and safety of other architectural elements (e.g. cornices, ornaments, chimneys, signs) | ERROR
Safety ratings: Low = Other architectural element(s) in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, element(s) are subject to damage but damage would not impede the function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
27. Safe conditions for movement outside the hospital buildings | ERROR
Safety ratings: Low = Obstacles or damage to structure or road and walkways will impede vehicle and pedestrian access to buildings or endanger pedestrians; Average = Obstacles or damage to structure or road and walkways will not impede pedestrian access, but will impede vehicle access; High = No obstacles, or potential for only minor or no damage that will not impede pedestrian or vehicle access.
28. Safe conditions for movement inside the building (e.g. corridors, stairs) | ERROR
Safety ratings: Low = Obstacles and damage to element(s) will impede movement inside the building and endanger occupants; Average = Obstacles or damage to elements will not impede movement of people but will impede movement of stretchers, wheeled equipment; High = No obstacles, potential for no or minor damage which will not impede movement of people or wheeled equipment.
29. Condition and safety of internal walls and partitions | ERROR
Safety ratings: Low = Internal walls and partitions in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, element(s) are subject to damage but damage would not impede the function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
30. Condition and safety of false or suspended ceilings | BLANK
Safety ratings: Low = False or suspended ceilings in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, element(s) subject to damage but damage would not impede the function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
IF THE HOSPITAL DOES NOT HAVE FALSE OR SUSPENDED CEILINGS, LEAVE BOXES BLANK.
31. Condition and safety of the elevator system | BLANK
Safety ratings: Low = Elevator system in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, element(s) subject to damage but damage would not impede the function of this and other elements, systems or operations; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
IF THERE ARE NO ELEVATORS, LEAVE BOXES BLANK.
32. Condition and safety of stairways and ramps | BLANK
Safety ratings: Low = In poor condition, subject to damage or there are obstacles, which would impede the function of this and other elements, systems or operations; Average = In fair condition, subject to damage but damage and obstacles would not impede the function of this and other elements, systems or operations; High = In good condition, no obstacles, potential for no or minor damage that would impede the function of this and other elements, systems or operations.
IF THERE ARE NO STAIRS AND RAMPS, LEAVE BOXES BLANK.
33. Condition and safety of floor coverings | ERROR
Safety ratings: Low = Floor coverings in poor condition, subject to damage which would impede the function of this and other elements, systems or operations; Average = In fair condition, subject to damage but damage would not impede function; High = In good condition, no or minor potential for damage that would impede the function of this and other elements, systems or operations.
3.2 Infrastructure protection, access and physical security | Control | Safety level
|  | Low | Average | High
34. Location of hospital’s critical services and equipment in relation to local hazards | ERROR
Safety ratings: Low = No protection measures taken; subject to damage, failure and disruption of critical services and hospital operations in emergencies and disasters; Average = Partial measures to protect critical services from local hazards are taken; subject to damage with some disruption of critical services and hospital operations in emergencies or disasters; High = Many measures are taken to protect critical services; high probability that critical services and hospital will operate with no or limited disruption in emergencies and disasters.
35. Hospital access routes | ERROR
Safety ratings: Low = Access routes subject to obstacles and damage that would impede access and the function of other elements, systems or operations; Average = Access routes subject to some obstacles and damage that would not impede access and function; High = No or minor potential for obstacles or damage that would impede access and the function of other elements, systems or operations.
36. Emergency exits and evacuation routes | ERROR
Safety ratings: Low = Exit and evacuation routes are not clearly marked and many are blocked; Average = Some exit and evacuation routes are marked and most are clear of obstacles; High = All exit and evacuation routes are clearly marked and free of obstacles.
37. Physical security of building, equipment, staff and patients | ERROR
Safety ratings: Low = No measures are in place; Average = Some physical security protection is in place (e.g. locked storage for supplies and equipment, asset tracking and inventory control); High = Wide range of security measures in place (e.g. design and layout, physical barriers, access control and door security systems, locked storage for supplies and equipment).
3.3 Critical systems | Control | Safety level
|  | Low | Average | High
3.3.1 Electrical systems
38. Capacity of alternative sources of electricity (e.g. generators) | ERROR
Safety ratings: Low = Alternate source(s) is (are) missing, or covers less than 30% of demand in critical areas, or can only be started manually; Average = Alternate source(s) covers 31–70% of demand in critical areas and starts automatically in less than 10 seconds in critical areas; High = Alternate source(s) start(s) automatically in less than 10 seconds and cover(s) more than 70% of demand in critical areas.
39. Regular tests of alternative sources of electricity in critical areas | ERROR
Safety ratings: Low = Tested at full load every 3 months or more; Average = Tested at full load every 1 to 3 months; High = Tested at full load at least monthly.
40. Condition and safety of alternative source(s) of electricity | ERROR
Safety ratings: Low = No alternate sources; generators are in poor condition;, there are no protective measures; Average = Generators are in fair condition; some measures provide partial protection and security; High = Generators are in good condition, well-secured and in good working order for emergencies.
41. Condition and safety of electrical equipment, cables and cable ducts | ERROR
Safety ratings: Low = Electrical equipment, power lines, cables and ducts are in poor condition, there are no protective measures; Average = Electrical equipment, power lines, cables and ducts are in fair condition; some measures provide partial protection and security; High = Electrical equipment, power lines, cables and ducts are in good condition, well-secured and in good working order.
42. Redundant system for the local electric power supply | ERROR
Safety ratings: Low = There is only one entrance for the local power supply; Average = There are two entrances for the local power supply; High = There are more than two entrances for the local power supply.
43. Condition and safety of control panels, overload breaker switches and cables | ERROR
Safety ratings: Low = Control panels or other elements are in poor condition, there are no protective measures; Average = Control panels or other elements are in fair condition; some measures provide partial protection; High = Control panels or other elements are in good condition, well-protected and in good working order.
44. Lighting system for critical areas of the hospital | ERROR
Safety ratings: Low = Poor level of lighting; there are no protective measures; Average = Lighting is satisfactory in the critical areas; some measures provide partial protection; High = Good levels of lighting and protection measures in place.
45. Condition and safety of internal and external lighting systems | ERROR
Safety ratings: Low = Internal and external lighting systems are in poor condition, there are no protective measures; Average = In fair condition; some measures provide partial protection; High = In good condition, well-protected and in good working order.
46. External electrical systems installed for hospital usage | ERROR
Safety ratings: Low = No electrical substations installed for hospital demands; Average = Substations installed; some measures provide partial protection, but would be vulnerable to damage or disruption, do not provide enough power to the hospital; High = Electrical substations installed, well-protected, and provide enough power to the hospital in an emergency or disaster.
47. Emergency maintenance and restoration of electric power supply and alternative sources | ERROR
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, but resources are not available; High = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
3.3.2 Telecommunication systems
48. Condition and safety of antennas | BLANK
Safety ratings: Low = Antennas and bracing in poor condition, there are no protective measures; Average = Antennas and bracing are in fair condition, some measures provide partial protection; High = Antennas and bracing are in good condition, well-secured and protection measures are in place.
IF THERE ARE NO ANTENNAS, LEAVE BOXES BLANK.
49. Condition and safety of low- and extra-low-voltage systems (Internet and telephone) | ERROR
Safety ratings: Low = Low voltage systems in poor condition, there are no protective measures; Average = Low voltage systems in fair condition, some measures provide partial protection; High = Good condition, well-secured and other protection measures in place.
50. Alternative communication systems | ERROR
Safety ratings: Low = Alternate communications systems do not exist, are in poor condition, or do not function; Average = Hospital-wide alternate communications system in fair condition, but is not tested on an annual basis; High = Alternate communication system in good condition and tested at least annually.
51. Condition and safety of telecommunications equipment and cables | ERROR
Safety ratings: Low = Telecommunications equipment and cables are in poor condition; there are no protective measures; Average = Equipment and cables are in fair condition; some measures provide partial protection; High = In good condition, well-secured and protected from hazards.
52. Effect of external telecommunications systems on hospital communications | ERROR
Safety ratings: Low = External telecommunications systems cause major interference with hospital communications; Average = External telecommunications system cause moderate interference with hospital communications; High = External communications cause no interference with hospital communications.
53. Safety of sites for telecommunication systems | ERROR
Safety ratings: Low = Sites for telecommunications systems are in poor condition, at high risk of failure due to hazards; there are no protective measures; Average = Sites in fair condition; some measures provide partial protection; High = Good condition, well-secured and other protective measures in place.
54. Condition and safety of internal communications systems | ERROR
Safety ratings: Low = Internal communications systems do not exist or are in poor condition; Average = Internal communications systems are in fair condition, but there are no alternate systems; High = Internal communications and back-up systems are in good working order.
55. Emergency maintenance and restoration of standard and alternate communications systems | ERROR
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, but resources are not available; High = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
3.3.3 Water supply system
56. Water reserves for hospital services and functions | ERROR
Safety ratings: Low = Sufficient for 24 hours or less, or water tank does not exist; Average = Sufficient for more than 24 hours but less than 72 hours; High = Guaranteed to cover at least 72 hours.
57. Location of water storage tanks | BLANK
Safety ratings: Low = The site is vulnerable with high risk of failure (e.g. structural, architectural and/or system vulnerabilities); Average = The site is exposed to moderate risk of failure (e.g. structural, architectural and/or system vulnerabilities); High = The site is not exposed to visually identifiable risks (e.g. structural, architectural and/or system vulnerabilities).
IF THE HOSPITAL DOES NOT HAVE A WATER STORAGE TANK, LEAVE BOXES BLANK.
58. Safety of the water distribution system | ERROR
Safety ratings: Low = Less than 60% are in good operational condition; Average = Between 60% and 80% are in good condition; High = Above 80% are in good condition.
59. Alternative water supply to the regular water supply | ERROR
Safety ratings: Low = Provides less than 30% of daily demand in an emergency or disaster scenario; Average = Provides 30−80% of daily demand in an emergency or disaster scenario; High = Provides more than 80% of daily demand in an emergency or disaster scenario.
60. Supplementary pumping system | ERROR
Safety ratings: Low = There is no back-up pump and operational capacity does not meet minimum daily demand; Average = Supplementary pumps are in fair condition but would not meet the minimum daily demand for water; High = All supplementary pumps and back-up systems are operational and would meet the minimum demand for water.
61. Emergency maintenance and restoration of water supply | ERROR
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, but resources are not available; High = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
3.3.4 Fire protection system
62. Condition and safety of the fire protection (passive) system | ERROR
Safety ratings: Low = Element(s) are subject to damage, and damage would impede the function of this and other elements, systems or operations; Average = Element(s) are subject to damage but damage would not impede function; High = No or minor potential for damage that would impede the function of this and other elements, systems or operations.
63. Fire/smoke detection systems | ERROR
Safety ratings: Low = No system has been installed; Average = System is partially installed, or infrequently maintained and tested; High = System is installed and well-maintained and tested frequently.
64. Fire suppression systems (automatic and manual) | ERROR
Safety ratings: Low = No system has been installed; inspections do not occur; Average = System is partially installed, or system is installed, but no maintenance or testing; inspections are incomplete or outdated; High = System is fully installed and regularly maintained and tested frequently; inspections are complete and up to date.
65. Water supply for fire suppression | ERROR
Safety ratings: Low = A source of permanent supply which could be used for fire suppression does not exist; Average = A source of permanent supply of water is available for fire suppression; there is limited capacity available, and no maintenance and testing has been conducted; High = A source of permanent water supply with significant capacity for fire suppression is available, regularly maintained and frequently tested.
66. Emergency maintenance and restoration of the fire protection system | ERROR
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, but resources are not available; High = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
3.3.5 Waste management systems
67. Safety of nonhazardous wastewater systems | ERROR
Safety ratings: Low = System for nonhazardous wastewater disposal does not exist or is in poor condition; Average = System is in fair condition, but little or no evidence of compliance and maintenance; High = Wastewater disposal system is in good condition with good capacity and evidence of compliance and maintenance.
68. Safety of hazardous wastewater and liquid waste | ERROR
Safety ratings: Low = System for hazardous wastewater disposal does not exist or is in poor condition; Average = System in fair condition but little or no evidence of compliance and maintenance; High = Disposal system has good capacity and evidence of compliance and maintenance.
69. Safety of nonhazardous solid waste system | ERROR
Safety ratings: Low = System for solid waste disposal does not exist or is in poor condition; Average = System is in fair condition, but little or no evidence of compliance and maintenance; High = Disposal system is in good condition with good capacity and evidence of compliance and maintenance.
70. Safety of hazardous solid waste system | ERROR
Safety ratings: Low = System for hazardous waste disposal does not exist or is in poor condition; Average = System is in fair condition but little or no evidence of compliance and maintenance; High = Disposal system is in good condition with good capacity and evidence of compliance and maintenance.
71. Emergency maintenance and restoration of all types of hospital waste management systems | ERROR
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, but resources are not available; High = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
3.3.6 Fuel storage systems (e.g. gas, gasoline, and diesel)
72. Fuel reserves | ERROR
Safety ratings: Low = Sufficient for 24 hours or less, or fuel tank does not exist; Average = Sufficient for more than 24 hours but less than 72 hours; High = Guaranteed to cover at least 72 hours.
73. Condition and safety of above-ground fuel tanks and/or cylinders | BLANK
Safety ratings: Low = Tanks are in poor condition; there are no anchors or tank enclosure; tanks are not safely located with respect to hazards; Average = Tanks are in fair condition, anchors and bracing are inadequate for major hazards; tank enclosure has some safety and security measures; High = Tanks are in good condition; anchors and bracing are in good condition for major hazards; the tank enclosure has adequate safety and security.
IF THE HOSPITAL DOES NOT HAVE THESE SERVICES, LEAVE BLANK.
74. Safe location of fuel storage away from hospital buildings | BLANK
Safety ratings: Low = Fuel storage is not accessible and is not located in a secure site; Average = Site in fair condition and in fair location in relation to hazards; some measures provide partial protection; High = In good condition and good location, well-secured and other protection measures in place; fuel tanks are accessible.
IF THERE IS NO FUEL TANK, LEAVE BOXES BLANK.
75. Condition and safety of the fuel distribution system (valves, hoses, and connections) | BLANK
Safety ratings: Low = Less than 60% of the system is in safe operational condition; Average = between 60% and 90% of the system is in good operational condition and has automatic shut-off valves; High = More than 90% of the system is in good operational condition and has automatic shut-off valves.
IF THERE IS NO FUEL DISTRIBUTION TANK, LEAVE BOXES BLANK.
76. Emergency maintenance and restoration of fuel reserves | ERROR
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, but resources are not available; High = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
3.3.7 Medical gases systems
77. Location of storage areas for medical gases | ERROR
Safety ratings: Low = No sites reserved for medical gases, or sites for medical gases are at high risk of failure due to hazards; there are no protective measures, and storage is not accessible; Average = Reserved areas in fair condition and fair location; some measures provide partial protection; High = In good condition, well-secured and other protective measures are in place; storage is accessible.
78. Safety of storage areas for the medical gas tanks and/or cylinders | ERROR
Safety ratings: Low = Medical gas tanks and cylinders in storage areas are poor condition; no protection measures, not secured; personnel are not trained to operate medical gas and fire extinguishing equipment; Average = Medical gas tanks and cylinders in storage areas are in fair condition, some measures provide partial protection; the quality of anchors and braces is inadequate; personnel are trained to operate equipment; High = Good condition, well-secured and protected, anchors are of good quality for major hazards; medical gas and fire extinguishing equipment operated by qualified personnel.
79. Condition and safety of medical gas distribution system (e.g. valves, pipes, connections) | ERROR
Safety ratings: Low = Less than 60% of the system is in good working condition; Average = Between 60% and 80% of the system is in good working condition; High = More than 80% of the system is in good working condition.
80. Condition and safety of medical gas cylinders and related equipment in the hospital | ERROR
Safety ratings: Low = Medical gas tanks and cylinders in hospital areas are in poor condition, no protective measures; not secured; Average = Medical gas tanks and cylinders are in fair condition; the quality of anchors and braces is inadequate; some measures provide partial protection; High = Good condition, well-secured and protected; anchors are of good quality for major hazards.
81. Availability of alternative sources of medical gases | ERROR
Safety Ratings: Low = Alternative sources are not available; Average = Alternative sources in place but delivery of supplies takes longer than 15 days; High = Sufficient alternative sources are available at short notice (less than 15 days).
82. Emergency maintenance and restoration of medical gas systems. | ERROR
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, and personnel have been trained, but resources are not available; High = Procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
3.3.8 Heating, ventilation, and air-conditioning (HVAC) systems
83. Adequate location of enclosures for HVAC equipment | ERROR
Safety ratings: Low = HVAC enclosures are not accessible and they are not located in a safe site; there are no protective measures; Average = HVAC enclosures are accessible, located at a safe site; some measures provide partial protection from hazards; High = HVAC enclosures are accessible, in a safe location and protected from hazards.
84. Safety of enclosures for HVAC equipment | ERROR
Safety ratings: Low = HVAC equipment is not accessible; no protective measures for safe operation and maintenance; Average = HVAC is accessible; some measures provide partial protection; High = HVAC equipment is accessible, wide range of protection measures in place.
85. Safety and operating condition of HVAC equipment (e.g. boiler, exhaust) | ERROR
Safety ratings: Low = HVAC equipment in poor condition, not maintained; Average = HVAC equipment in fair condition; some measures provide partial protection, but no regular maintenance; High = Good condition, well-secured and protected from hazards (e.g. anchors are of good quality); regular maintenance and testing of controls and alarms conducted.
86. Adequate supports for ducts and review of flexibility of ducts and piping that cross expansion joints | ERROR
Safety ratings: Low = Supports are lacking and connections are rigid; Average = Supports are in fair condition or connections are flexible; High = Supports are in good condition and connections are flexible.
87. Condition and safety of pipes, connections and valves | ERROR
Safety ratings: Low = Less than 60% of pipes are in good condition; limited protective measures against hazards; Average = Between 60% and 80% are in good condition; some measures provide partial protection against hazards; High = Above 80% are in good condition and are well-secured and protected against hazards.
88. Condition and safety of air-conditioning equipment | ERROR
Safety ratings: Low = Air-conditioning units in poor condition, not secured; Average = Air-conditioning units are in fair condition; some measures provide partial protection (e.g. quality of anchors and braces is inadequate); High = Good condition, well-secured and protected from hazards (e.g. anchors are of good quality).
89. Operation of air-conditioning system (including negative pressure areas) | ERROR
Safety ratings: Low = Air-conditioning system has no capability for establishing zones of the hospital; Average = Air-conditioning system can establish zones, but has no capacity to separate air circulating between high-risk areas and other areas of the hospital; High = Air-conditioning system can isolate air from high-risk areas; negative pressure rooms are available.
90. Emergency maintenance and restoration of the HVAC systems | ERROR
Safety ratings: Low = Documented procedures and maintenance/inspection records do not exist; Average = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, but resources are not available; High = Documented procedures exist, maintenance/inspection records are up to date, personnel have been trained, and resources are in place for implementing emergency maintenance and restoration.
3.4 Equipment and supplies | Control | Safety level
|  | Low | Average | High
3.4.1 Office and storeroom furnishings and equipment (fixed and movable)
91. Safety of shelving and shelf contents | ERROR
Safety ratings: Low = Shelving is not safely located (or in seismic and wind-prone areas not attached to walls in in more than 20% of cases); Average = Shelving is safely located (and attached to walls in seismic and wind-prone areas) and contents are secured in 20−80% of cases; High = More than 80% of shelving and the contents of shelves are safely located, attached to walls, and contents are secured.
92. Safety of computers and printers | ERROR
Safety ratings: Low = No measures to protect computers from hazards are in place; Average = Computers are in safe locations, some measures offer partial protection from hazards; High = Computers are in safe locations, well-secured and good protective measures in place.
3.4.2 Medical and laboratory equipment and supplies used for diagnosis and treatment
93. Safety of medical equipment in operating theatres and recovery rooms | ERROR
Safety ratings: Low = The operating theatres are in an unsafe location, equipment is lacking or in poor condition or there are no protective measures; Average = The operating theatres are in a safe location, equipment is in fair condition, and some measures provide partial protection; High = Operating theatres are in a safe location, equipment is in good condition, is well-secured and measures provide protection.
94. Condition and safety of radiology and imaging equipment | ERROR
Safety ratings: Low = The radiology and imaging equipment is not in a safe location, equipment is lacking or in poor condition, or there are no protective measures; Average = The equipment is in a safe location, is in fair condition, and some measures offer partial protection; High = Equipment is in a safe location, is in good condition, well-secured and measures provide good protection.
95. Condition and safety of laboratory equipment and supplies | ERROR
Safety ratings: Low = Biosafety measures are poor, laboratory equipment is lacking or in poor condition, or there are no protective measures; Average = Biosafety measures are in place, the equipment is in fair condition, and some measures provide partial protection; High = Biosafety measures in place, equipment is in good condition, well-secured and measures provide good protection.
96. Condition and safety of medical equipment in emergency care services unit | ERROR
Safety ratings: Low = The medical equipment is lacking or in poor condition, or there are no protective measures; Average = The equipment is in fair condition and some measures provide partial protection; High = Equipment is in good condition, well-secured and measures provide good protection.
97. Condition and safety of medical equipment in intensive or intermediate care unit | ERROR
Safety ratings: Low = The medical equipment is lacking or in poor condition, or there are no protective measures; Average = The equipment is in fair condition and some measures provide partial protection; High = Equipment is in good condition, is well-secured and measures provide good protection.
98. Condition and safety of equipment and furnishings in the pharmacy | ERROR
Safety ratings: Low = The equipment in the pharmacy is lacking or in poor condition, or there are no protective measures; Average = The equipment is in fair condition and some measures provide partial protection; High = Equipment is in good condition, is well-secured and measures provide good protection.
99. Condition and safety of equipment and supplies in the sterilization services | ERROR
Safety ratings: Equipment is lacking or in poor condition, or there are no protective measures; Average = Equipment is in fair condition and some measures provide partial protection; High = Equipment is in good condition, is well-secured and measures provide good protection.
100. Condition and safety of medical equipment for obstetric emergencies and neonatal care | ERROR
Safety ratings: Low = Equipment is lacking or in poor condition, or there are no protective measures; Average = Equipment is in fair condition and some measures provide partial protection; High = Equipment is in good condition, is well-secured and measures provide good protection.
101. Condition and safety of medical equipment and supplies emergency care for burns | ERROR
Safety ratings: Low = Equipment is lacking, is in poor condition, or there are no protective measures; Average = Equipment is in fair condition and some measures provide partial protection; High = Equipment is in good condition, is well-secured and measures provide good protection.
102. Condition and safety of medical equipment for nuclear medicine and radiation therapy | BLANK
Safety ratings: Low = Equipment is lacking, is in poor condition, or there are no protective measures; Average = Equipment is in fair condition and some measures provide partial protection; High = Equipment is in good condition, is well-secured and measures provide good protection.
IF THE HOSPITAL DOES NOT HAVE THESE SERVICES, LEAVE BLANK.
103. Condition and safety of medical equipment in other services | ERROR
Safety ratings: Low = More than 30% of equipment is at risk of material or functional failure and/or equipment puts the entire service’s operation at direct or indirect risk; Average = Between 10% and 30% of equipment is at risk of loss; High = Less than 10% of equipment is at risk of loss.
104. Medicines and supplies | ERROR
Safety ratings: Low = Nonexistent; Average = Supply covers less than 72 hours at maximum capacity; High = Supply guaranteed for at least 72 hours at maximum hospital capacity.
105. Sterilized instruments and other materials | ERROR
Safety ratings: Low = Nonexistent; Average = Supply cover less than 72 hours at maximum capacity; High = Supply is guaranteed for at least 72 hours at maximum hospital capacity.
106. Medical equipment specifically used in emergencies and disasters | ERROR
Safety ratings: Low = Nonexistent; Average = Supply covers less than 72 hours at maximum hospital capacity; High = Supply guaranteed for at least 72 hours at maximum hospital capacity.
107. Supply of medical gases | ERROR
Safety ratings: Low = Less than 10 days’ supply; Average = Supply for between 10 and 15 days; High = Supply for at least 15 days.
108. Mechanical volume ventilators | ERROR
Safety ratings: Low = Nonexistent; Average = Supply covers less than 72 hours at maximum hospital capacity; High = Supply guaranteed for at least 72 hours at maximum hospital capacity.
109. Electromedical equipment | ERROR
Safety ratings: Low = Nonexistent; Average = Supply covers less than 72 hours at maximum hospital capacity; High = Supply guaranteed for at least 72 hours at maximum hospital capacity.
110. Life-support equipment | ERROR
Safety ratings: Low = Nonexistent; Average = Supply covers less than 72 hours at maximum hospital capacity; High = Supply guaranteed for at least 72 hours at maximum hospital capacity.
111. Supplies, equipment or crash carts for cardiopulmonary arrest | ERROR
Safety ratings: Low = Nonexistent; Average = Supplies and equipment for cardiopulmonary emergencies (or crash carts) in good condition but cover less than 72 hours at maximum hospital capacity; High = Supplies and equipment for cardiopulmonary emergencies (or crash carts) guaranteed in good condition and adequate supplies for at least 72 hours at maximum hospital capacity.
MODULE 4. Emergency and disaster management
4.1 Coordination of emergency and disaster management activities | Control | Safety level
|  | Low | Average | High
112. Hospital Emergency/Disaster Committee | ERROR
Safety ratings: Low = Committee does not exist, or 1–3 departments or disciplines represented; Average = Committee exists with 4–5 departments or disciplines represented, but is not fulfilling functions effectively; High = Committee exists with 6 or more departments or disciplines represented and is fulfilling functions effectively.
113. Committee member responsibilities and training | ERROR
Safety ratings: Low = Committee does not exist or members are untrained and responsibilities not assigned; Average = Members have received training and have been officially assigned; High = All members are trained and are actively fulfilling their roles and responsibilities.
114. Designated emergency and disaster management coordinator | ERROR
Safety ratings: Low = There is no staff member who has been assigned responsibilities as the emergency/disaster management coordinator; Average = Emergency/disaster management coordination tasks have been assigned to a staff member, but it is not his/her main task; High = A staff member is assigned the emergency and disaster management coordination responsibilities as his/her main task, and is fulfilling the role of implementing the hospital’s preparedness programme.
115. Preparedness programme for strengthening emergency and disaster response and recovery | ERROR
Safety ratings: Low = A programme for strengthening preparedness, response and recovery does not exist or, if it exists, no preparedness activities are being implemented; Average = A programme for strengthening preparedness, response and recovery exists and some activities are being implemented; High = A programme for strengthening preparedness, response and recovery is being fully implemented under the leadership of the Hospital Emergency/Disaster Committee.
116. Hospital incident management system | ERROR
Safety ratings: Low = No arrangements for hospital incident management exist; Average = Staff assigned to key hospital incident management positions but with no written procedures to operationalize its functions; High = Hospital incident management procedures exist and are fully operational with properly trained personnel to assume different coordination roles and responsibilities.
117. Emergency Operations Centre (EOC) | ERROR
Safety ratings: Low = The EOC is not designated or is in an unsafe or insecure location; Average = The designated EOC is in a safe, secure and accessible location, but would have limited operational capacity immediately in an emergency; High = The EOC is in a safe, secure and accessible location with immediate operational capacity.
118. Coordination mechanisms and cooperative arrangements with local emergency/disaster management agencies | ERROR
Safety ratings: Low = No arrangements exist; Average = Arrangements exist but are not fully operational; High = Arrangements exist and are fully operational.
119. Coordination mechanisms and cooperative arrangements with the health-care network | ERROR
Safety ratings: Low = No arrangements exist; Average = Arrangements exist but are not fully operational; High = Arrangements exist and are fully operational.
4.2 Hospital emergency and disaster management response and recovery planning | Control | Safety level
|  | Low | Average | High
120. Hospital emergency or disaster response plan | ERROR
Safety ratings: Low = Plan is not documented; Average = Documented plan is complete, but is not easily accessible, not up to date (more than 12 months since the last update); High = Plan is complete, easily accessible, reviewed/updated at least annually, and resources are available to implement the plan.
121. Hazard-specific subplans | ERROR
Safety ratings: Low = Hazard-specific response subplans are not documented; Average = Documented plans are complete but not easily accessible, not up to date (more than 12 months since last review/update); High = Documented plans are complete, reviewed/updated at least annually, and resources are available to implement the plans.
122. Procedures to activate and deactivate plans | ERROR
Safety ratings: Low = Procedures do not exist or exist only as a document; Average = Procedures exist, personnel have been trained, but procedures are not updated or tested annually; High = Up-to-date procedures exist, personnel have been trained, and procedures have been tested at least annually.
123. Hospital emergency and disaster response plan exercises, evaluation and corrective actions | ERROR
Safety ratings: Low = Response plan and subplans have not been tested; Average = Response plan or subplans are tested, but are not tested at least annually; High = Response plan or subplans are tested at least annually and updated according to the exercise results.
124. Hospital recovery plan | ERROR
Safety ratings: Low = Recovery plan is not documented; Average = Documented plan is complete but not easily accessible, not up to date (more than 12 months since last review/update); High = Documented plan is complete, easily accessible, and reviewed/updated at least annually.
4.3 Communication and information management | Control | Safety level
|  | Low | Average | High
125. Emergency internal and external communication | ERROR
Safety ratings: Low = Central internal and external communication system functions inconsistently or incompletely; operators are not trained in emergency communication; Average = System functions appropriately, operators have received some training in emergency communication, tests are not conducted at least annually; High = System functions completely and operators are fully trained in emergency use, and tests of the system are conducted at least annually.
126. External stakeholder directory | ERROR
Safety ratings: Low = Directory of external stakeholders does not exist; Average = Directory exists but is not current (more than 3 months since it was updated); High = Directory is available, is up to date and is held by key emergency response staff.
127. Procedures for communicating with the public and media | ERROR
Safety ratings: Low = Procedures do not exist, no spokesperson nominated; Average = Procedures exist and nominated spokespersons have been trained; High = Procedures exist, nominated spokespersons have been trained, and procedures have been tested at least annually.
128. Management of patient information | ERROR
Safety ratings: Low = Procedures for emergency situations do not exist; Average = Procedures for emergency situations exist and personnel have been trained but no resources are available; High = Procedures for emergency situations exist, personnel have been trained, and resources are in place for implementation.
4.4 Human resources | Control | Safety level
|  | Low | Average | High
129. Staff contact list | ERROR
Safety ratings: Low = Contact list does not exist; Average = List exists, but is not current (more than 3 months since it was updated); High = List is available and up to date.
130. Staff availability | ERROR
Safety ratings: Low = Less than 50% of staff are available to run each department adequately; Average = 50−80% of staff are available; High = 80−100% of staff are available.
131. Mobilization and recruitment of personnel during an emergency or disaster | ERROR
Safety ratings: Low = Procedures do not exist or exist only in a document; Average = Procedures exist and personnel have been trained, but the human resources for an emergency situation are not available; High = Procedures exist, personnel have been trained, and the human resources are available to meet anticipated needs in an emergency.
132. Duties assigned to personnel for emergency or disaster response and recovery | ERROR
Safety ratings: Low = Emergency assignments do not exist or are not documented; Average = Duties are identified, some (but not all) personnel receive written assignments or training; High = Written duties are assigned, and training or an exercise is conducted for all personnel at least annually.
133. Well-being of hospital personnel during an emergency or disaster | ERROR
Safety ratings: Low = A designated space and measures do not exist; Average = Space has been designated, but measures cover less than 72 hours; High = Measures are ensured for at least 72 hours.
4.5 Logistics and finance | Control | Safety level
|  | Low | Average | High
134. Agreements with local suppliers and vendors for emergencies and disasters | ERROR
Safety ratings: Low = No arrangements exist; Average = Arrangements exist, but are not fully operational; High = Arrangements exist and are fully operational.
135. Transportation during an emergency | ERROR
Safety ratings: Low = Ambulances and other vehicles and modes of transportation are not available; Average = Some vehicles are available, but not in sufficient numbers for a major emergency or disaster; High = Appropriate vehicles in sufficient numbers are available during emergencies/disasters.
136. Food and drinking-water during an emergency | ERROR
Safety ratings: Low = Procedures for food and drinking-water for emergencies are non-existent; Average = Procedures exist, food and drinking-water is guaranteed for less than 72 hours; High = Food and drinking-water for emergencies is guaranteed for at least 72 hours.
137. Financial resources for emergencies and disasters | ERROR
Safety ratings: Low = Emergency budget or mechanism to access emergency funds is not in place; Average = Funds are budgeted and mechanisms are available but cover less than 72 hours; High = Sufficient funds are guaranteed for 72 hours or more.
4.6 Patient care and support services | Control | Safety level
|  | Low | Average | High
138. Continuity of emergency and critical care services | ERROR
Safety ratings: Low = Procedures do not exist or exist only as a document; Average = Procedures exist, personnel have been trained but would not be available at all times; High = Procedures exist, personnel have been trained, and resources are available to implement procedures at maximum hospital capacity for emergency and disaster situations at all times.
139. Continuity of essential clinical support services | ERROR
Safety ratings: Low = Procedures do not exist or exist only as a document; Average = Procedures exists and personnel have been trained but would not be available at all times; High = Procedures exists, personnel have been trained, and resources are available to implement procedures at maximum hospital capacity for emergency and disaster situations at all times.
140. Expansion of usable space for mass casualty incidents | ERROR
Safety ratings: Low = Space for expansion has not been identified; Average = Space has been identified; equipment, supplies and procedures are available to carry out the expansion and staff have been trained, but testing has not been conducted; High = Procedures exist and have been tested, personnel have been trained, and equipment, supplies and other resources are available to carry out the expansion of space.
141. Triage for major emergencies and disasters | ERROR
Safety ratings: Low = Designated triage location or procedures do not exist; Average = Triage location and procedures exist and personnel have been trained, but procedures have not been tested for emergency and disaster situations; High = Location and procedures exist and have been tested, personnel have been trained, and resources are in place to implement at maximum hospital capacity in emergency and disaster situations.
142. Triage tags and other logistical supplies for mass casualty incidents | ERROR
Safety ratings: Low = Nonexistent; Average = Supply covers less than 72 hours of maximum hospital capacity; High = Supply guaranteed for at least 72 hours of maximum hospital capacity.
143. System for referral, transfer and reception of patients | ERROR
Safety ratings: Low = Procedures do not exist or exist only as a document; Average = Procedures exist and personnel have been trained, but procedures have not been tested for emergency or disaster situations; High = Procedures exist and have been tested, personnel have been trained, and resources are available to implement measures at maximum hospital capacity in emergency or disaster situations.
144. Infection surveillance, prevention, and control procedures | ERROR
Safety ratings: Low = Policies and procedures do not exist; standard precautions for infection prevention and control are not followed routinely; Average = Policies and procedures exist, standard precautions are routinely followed, personnel have been trained, but the level of resources required for emergency and disaster situations, including epidemics, is not available; High = Policies and procedures exist, infection prevention and control measures are in place, personnel have been trained, and resources are available to implement measures at maximum hospital capacity in emergency and disaster situations.
145. Psychosocial services | ERROR
Safety ratings: Low = Procedures do not exist or exist only as a document; Average = Procedures exist and personnel have been trained, but the level of resources required for emergency and disaster situations is not available; High = Procedures exist, personnel have been trained, and resources are available for implementation of procedures at maximum hospital capacity in emergency and disaster situations.
146. Post-mortem procedures in a mass fatality incident | ERROR
Safety ratings: Low = Procedures for a mass fatality incident do not exist or exist only as a document; Average = Procedures exist and personnel have been trained, but the level of resources required for emergency and disaster situations is not available; High = Procedures exist, personnel have been trained, and resources are available for implementation of procedures at maximum hospital capacity in emergency and disaster situations
4.7 Evacuation, decontamination and security | Control | Safety level
|  | Low | Average | High
147. Evacuation plan | ERROR
Safety ratings: Low = Plan does not exist or exists only as a document; Average = Plan exists and personnel have been trained in procedures, but tests are not conducted regularly; High = Plan exists, personnel have been trained, and evacuation drills are held at least annually.
148. Decontamination for chemical/biological hazards | ERROR
Safety ratings: Low = No personal protective equipment is available for immediate use by hospital staff, or no decontamination area exists; Average = Personal protective equipment is available for immediate use, decontamination areas are established, staff training and drills are not conducted annually; High = Personal protective equipment is available for immediate use, decontamination areas are established and personnel are trained and tested at least annually.
149. Personal protection equipment and isolation for infectious diseases and epidemics | ERROR
Safety ratings: Low = No personal protective equipment is available for immediate use by hospital staff, or no isolation area exists; Average = Supply is available for immediate use, but is sufficient for less than 72 hours of maximum hospital capacity, isolation areas are established, staff training and testing of procedures are not conducted annually; High = Supply is guaranteed for at least 72 hours of maximum hospital capacity and alternate sources are in place for resupply, isolation areas are established, staff training and testing of procedures are conducted at least annually.
150. Emergency security procedures | ERROR
Safety ratings: Low = Emergency security procedures do not exist or exist only as a document; Average = Documented procedures exist and personnel have been trained in emergency security procedures but testing is not conducted at least annually; High = Personnel are trained and tests of the documented procedures are held at least annually.
151. Computer system network security | ERROR
Safety ratings: Low = The hospital does not have a computer security system plan and procedures in place; Average = The hospital has a basic cyber security plan in place but it is not monitored and updated regularly; High = The hospital has a cyber security plan in place and it is updated regularly.
Step 2: Before moving on to the next step, ensure that there are no "ERROR".In case an "ERROR" message is shown, refer back to that specific question and answer it according to Step 3. Charts and formulas will not calculate properly if there are any "ERROR" messages.

## Calculator 2
Hospital Safety Index: Page 2_Step 3 (Summary of Safety Ratings)
Step 3 : Automatic Tabulation of Responses by Module
MODULE 2. Elements related to the structural safety of the hospital
| Number of items |  |  | Weighted contribution to module (%) |  |  |  | Weighted contribution to module (%)
| Low | Average | High | Low | Average | High | Total | Low | Average | High | Total
2.1 Prior events and hazards affecting building safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25
2.2 Building integrity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75
Total | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 100
MODULE 3: Elements related to the non-structural safety of the hospital
| Number of items |  |  | Weighted contribution to module (%) |  |  |  | Weighted contribution to module (%)
| Low | Average | High | Low | Average | High | Total | Low | Average | High | Total
3.1 Architectural safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23
3.2 Infrastructure protection, access and physical security | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
3.3 Critical systems | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 50
3.3.1 Electrical systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
3.3.2 Telecommunication systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
3.3.3 Water supply system | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
3.3.4 Fire protection system | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5
3.3.5 Waste management systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5
3.3.6 Fuel storage systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
3.3.7 Medical gases systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
3.3.8 Heating, ventilation, and air-conditioning (HVAC) systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
3.4 Equipment and supplies | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 17
3.4.1 Office and storeroom furnishings and equipment (fixed and movable) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7
3.4.2 Medical and laboratory equipment and supplies used for diagnosis and treatment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.3
Total | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 100
MODULE 4. Emergency and disaster management
| Number of items |  |  | Weighted contribution to module (%) |  |  |  | Weighted contribution to module (%)
| Low | Average | High | Low | Average | High | Total | Low | Average | High | Total
4.1 Coordination of emergency and disaster management activities | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15
4.2 Hospital emergency and disaster response planning | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18
4.3 Communication and information management | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7
4.4 Human resources | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20
4.5 Logistics and finance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
4.6 Patient care and support services | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25
4.7 Evacuation, decontamination and security | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7
Total | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 100

## Calculator 3
Hospital Safety Index: Page 3_Step 4-10 (Calculation of Module-specific Index and overall Hospital Safety Index)
1. Module-Specific Index
Step 4: Automatic tabulation of responses by module (summary of page 2)
MODULE | Unlikely to function (Safety level = low) | Likely to function (Safety level = average) | Highly likely to function (Safety level = high) | Total
Structural safety (MODULE 2) | 0 | 0 | 0 | 100
Nonstructural safety (MODULE 3) | 0 | 0 | 0 | 100
Emergency and disaster management (MODULE 4) | 0 | 0 | 0 | 100
Step 5: Input horizontal weights in the YELLOW cells which are to be used for this purpose. These will indicate relative safety levels between Low/Average/High in reference to High. It is proposed to use the figures below that were agreed by the WHO/PAHO - DIMAG to calibrate the individual module scores against a common point of reference. In this case, the relative safety levels are in the ratio of 1 : 2 : 4.
MODULE | Horizontal weight | Horizontal weight (example)
Unlikely to function | 0.25 | 0.25
Likely to function | 0.5 | 0.5
Highly likely to function | 1 | 1
Step 6: Automatic tabulation of CRUDE (non-bias adjusted) safety index by module
MODULE | Crude safety index
Structural safety (MODULE 2) | 0
Nonstructural safety (MODULE 3) | 0
Emergency and disaster management (MODULE 4) | 0
Step 7: Automatic calculation of the weight range to be used for bias adjustment in safety and vulnerability indexes
NOTE : In order to prevent bias due to random figures used in the module's weights, it was agreed to use a range that takes into account both extremes of the horizontal weight scale. In this case, the minimum level of safety is 0.25 and the maximum score is 1. Using a range also allows the evaluator to graphically appreciate these indexes and how they relate to each other. It has been suggested that these indexes could be viewed using the "glass half-empty/half-full" concept. The more safe the hospital becomes, vulnerability will be reduced or, in more words, the glass will get fuller.
Range = upper horizontal weight - lower horizontal weight = |  | 0.75
Step 8: Automatic calculation of ADJUSTED (bias-free) safety index and vulnerability index ny module. Formulas are below.
Safety index = | Crude safty index - Lower range limit
Range
Vulnerability index = | Upper range limit - Crude safety index
Range
MODULE | Safety index | Vulnerbaility index
Structural safety (MODULE 2) | 0 | 0
Nonstructural safety (MODULE 3) | 0 | 0
Emergency and disaster management (MODULE 4) | 0 | 0
Step 9: Automatic comparison of safety index with base recommendations
Safety index | Category | What should be done?
0 – 0,35 | c | Urgent intervention measures are needed. The hospital is unlikely to function during and after emergencies and disasters, and the hospital's current levels of safety and emergency and disaster management are inadequate to protect the lives of patients and hospital staff during and after emergencies.
0,36 – 0,65 | b | Intervention measures are needed in the short term. The hospital's current levels of safety and emergency and diaster management are such that the safety of patients and hospital staff, and the hospital's ability to function during and after emergencies and disasters are potentially at risk.
0,66 – 1 | a | It is likely that the hospital will function in emergencies and disasters. It is recommended, however, to continue with measures to improve emergency and disaster management response capacity and to carry out preventive measures in the medium- and long-term to improve the safety level in case of emergencies and disasters.
MODULE | health facility status
Structural safety (MODULE 2) | c
Nonstructural safety (MODULE 3) | c
Emergency and disaster management (MODULE 4) | c
2. Overall Safety Index
Step 10: To calculate overall safety index and vulnerability index, input the vertical weights in the YELLOW cells which are to be used for this purpose. They will indicate a percentage of contribution of a module to overall safety index (total weights of modules is 100%). Examples below are figures in the ratio of 5 : 3: 2 (model 1) and in the ratio of 1 : 1 : 1 (model 2). Model 1 is the ratio used in the original version of the HSI and could be considered for a group of hospitals which are at higher risk of structural failure in earthquakes or high winds. Model 2 is proposed for countries or regions where earthquakes and high winds are not considered to be likely hazards.
MODULE | Vertical weight | Vertical weight (model 1) | Vertical weight (model 2)
Structural safety | 33.33 | 50 | 33.3333
Nonstructural safey | 33.33 | 30 | 33.3333
Emergency and disaster management | 33.33 | 20 | 33.3333
Total (%) | 100 | 100 | 100
Step 11: Automatic tabulation of overall safety index.
Overall safety index = | 0
Safety index | Category | What should be done?
0 – 0,35 | C | Urgent intervention measures are needed. The hospital is unlikely to function during and after emergencies and disasters, and the hospital's current levels of safety and emergency and disaster management are inadequate to protect the lives of patients and hospital staff during and after emergencies.
0,36 – 0,65 | B | Intervention measures are needed in the short term. The hospital's current levels of safety and emergency and diaster management are such that the safety of patients and hospital staff, and the hospital's ability to function during and after emergencies and disasters are potentially at risk.
0,66 – 1 | A | It is likely that the hospital will function in emergencies and disasters. It is recommended, however, to continue with measures to improve emergency and disaster management response capacity and to carry out preventive measures in the medium- and long-term to improve the safety level in case of emergencies and disasters.
Step 12: Automatic comparison of overall safety index with base recommendations above.
Overall health facility status: | C

## Analysis
Hospital Safety Index |  |  |  | Category
Overall Index |  |  | 0% | C
Structural safety index |  |  | 0% | c
Non-structural safety index |  |  | 0% | c
Emergency and disaster management index |  |  | 0% | c
|  | Crude | Adjusted
Detailed analysis
Structural safety |  |  |  | Category
| Prior event | 0% | -33.33% | c
| Building integrity | 0% | -33.33% | c
Non-structural safety
| Architectural safety | 0% | -33.33% | c
| Infrastructure protection, access and physical security | 0% | -33.33% | c
| Critical systems | 0% | -33.33% | c
| Equipment and supplies | 0% | -33.33% | c
Emergency and disaster management index
| Coordination of emergency and disaster management activities | 0% | -33.33% | c
| Hospital emergency and disaster response planning | 0% | -33.33% | c
| Communication and information management | 0% | -33.33% | c
| Human resources | 0% | -33.33% | c
| Logistics and finance | 0% | -33.33% | c
| Patient care and support services | 0% | -33.33% | c
| Evacuation, decontamination and security | 0% | -33.33% | c
Further analysis (Non-structural safety)
Critical systems
| Electrical systems | 0% | -33.33% | c
| Telecommunication systems | 0% | -33.33% | c
| Water supply system | 0% | -33.33% | c
| Fire protection system | 0% | -33.33% | c
| Waste management systems | 0% | -33.33% | c
| Fuel storage systems | 0% | -33.33% | c
| Medical gases systems | 0% | -33.33% | c
| HVAC systems | 0% | -33.33% | c